Bidirectional high frequency isolation ACDC module（20kW/15kW）

【Abstract】

V2G (Vehicle to Grid),Its core idea is to realize the bidirectional between EV and Grid，use the energy storage of EV as a supplement to the grid and renewable energy;V2L (Vehicle to Load),EV with the bidirectional charging and discharging batteries can be used as mobile energy storage to supply grid for 220 or 380V AC loads, which are equivalent to large mobile power banks.

V2G is widely used in energy storage, battery capacity, emergency power supply, equipment aging and many other fields. It is the first choice for the energy bidirectional flow application industry.

【Highlight】

Safe and reliable

•High-frequency isolation for higher safety
•DSP+CPLD full digital control
•Multiple security protection

Flexible configuration

•Modular design for easy maintenance
•Support multi-module parallel expansion
•The system has on-off-grid switching function

Smart and friendly

•Ultra wide voltage range

•Intelligent fan speed regulation to reduce power consumption and noise

Low cost

•Compared with the traditional bidirectional power supply scheme, the power frequency transformer is saved, and the system cost is low

【Application】

•Energy storage (EV energy storage V2G)

•Energy storage (battery cascade utilization)

•Battery composition and capacity

•DC power aging

【Technical parameter】

| Product name |  | Bidirectional high frequency isolation ACDC module |  |
| --- | --- | --- | --- |
| Product model |  | BIM75040 | BIM300100 |
| Charge |  |  |  |
| AC side parameter | Rated grid voltage | 400Vac（380/400/415Vac） |  |
|  | Grid voltage range | 304Vac～485Vac |  |
|  | Grid voltage frequency | 50/60 ±5% (50Hz/60Hz self-adapting) |  |
|  | AC side | 3L+PE |  |
|  | AC input current | ≤38A | ≤29A |
|  | Power factor | ≥ 0.99 , full load |  |
|  | THD of Current | < 3% , full load |  |
| Battery side parameter | Voltage range | 60～750VDC , Rated voltage 500VDC | 40～300VDC , Rated voltage 150VDC |
|  | Output current | 40A | 100A |
|  | Rated power | 20kW | 15kW |
|  | Efficiency | 95% max （Using SiC）,94%（Using Si） |  |
|  | Voltage regulation accuracy | ±0.5% |  |
|  | Steady flow accuracy | ±1% |  |
|  | Ripple factor | <1%Vo |  |
| Discharge |  |  |  |
| Battery side parameter | Voltage range | 60～750VDC , Rated voltage 500VDC | 40～300VDC , Rated voltage 150VDC |
|  | Output current | 40A Max | 100A Max |
| AC side parameter | V2G（grid discharge） |  |  |
|  | Grid voltage range | 304Vac～485Vac |  |
|  | Grid voltage frequency | 50/60 ±5% (50Hz/60Hz self-adapting) |  |
|  | Rated power | 20kW | 15kW |
|  | Efficiency | 95% max（Using SiC）,94%（Using Si） |  |
| Other properties |  |  |  |
| Protect function | OV protection | Have |  |
|  | OC protection | Have |  |
|  | SC protection | Have |  |
|  | OT protection | Have |  |
| Other parameter | Operating temperature | -30～70 ℃ , 55℃ above output power derating |  |
|  | Storage temperature | -40～75 ℃ |  |
|  | Noise | <60dB |  |
|  | Dimension | 442*575*86mm (W*H*D) |  |
|  | Weight | 19Kg | 15Kg |
|  | Protection | IP20 |  |
|  | Type of cooling | Intelligent speed regulation, forced air cooling |  |
| Certification | EMC | 《GB/T 34120-2017》《GB/T 34133-2017》 《NB/T 33001-2018》《NB/T 33008-2018》 |  |